## Slide 1: MELCOR Code Validation for LPF Applications
David L.Y. Louie, Ph.D.
Email: dllouie@sandia.gov
Sandia National Laboratories
February 22, 2021
SAND2021-1838 C
EFCOG Nuclear Facility Workshop 2021
NSR&D Subgroup Session

## Slide 2: What is Leak Path Factor?
Five Factor Formula
    MAR - material at risk
    DR – damage ratio
    ARF – airborne release fraction
    RF – respirable fraction
    LPF – leak path factor
    ARF & RF from DOE-HDBK-3010
[DOE-HDBK-1224-2018]
Source Term (ST) [DOE-HDBK-1224-2018]
  BST- Building ST defines as IST∙LPF
  Respirable: ISTRF= IST∙RF, BSTRF = BST∙RF
LPF
  Computer code, such as MELCOR – more flexible
    Needs IST from the scenario, and building information, etc.

## Slide 3: MELCOR Code
  MELCOR is developed by Sandia National Laboratories
    US Nuclear Regulatory Commission (NRC)
      Developed initially for severe accident analysis of Light Water Reactors
    Since early 1980s
  MELCOR Development
    US NRC Cooperative Severe Accident Research Program (CSARP)
    Over 900+ licensed MELCOR users worldwide
    Light water reactor (LWR) research
    Advanced reactor development
    Nuclear fusion development
  MELCOR Application
    NRC licensing support
      Existing LWRs
      Advanced reactors
    Non-reactor support
      Nuclear fusion research
      Spent fuel reprocessing accident analysis
    DOE facility support
      MELCOR is designated as a Toolbox code for LPF analysis

## Slide 4: History of MELCOR uses in SBs
MELCOR is a DOE Toolbox code
MELCOR 1.8.5 LPF guidance and gap analysis reports (2004)
MELCOR 1.8.5 and 1.8.6 have been used for LPF analyses (2000+)
  To support the facility DSA at:
  LANL – PF4(TA-55), WCRRF, DVRSF, CMRR, BTF
  LLNL – Plutonium facility (331)
  NNSS– Device Assembly Facility, Area G Tunnel
  Pantex
  SRNL – K Area Spent Fuel Storage Facility
MELCOR 2.0 or later version (today)
  LANL PF4

## Slide 5: MELCOR V&V
DOE NSR&D Program
NSRD-10 project was done to supplement the 2004 MELCOR 1.8.5 guidance report
  Use latest MELCOR version (2.1)
  Validation tests
    Reactor and non-reactor experiments, particularly for aerosol physics
    Analytical tests
  Verification tests
    Version-to-version comparison – MELCOR 1.8.5, 1.8.6 and 2.1
    Additional verification beyond those in MELCOR 1.8.5 guidance report
  Best practices for common accident scenarios at DOE facilities

## Slide 6: NSRD-10 V&V Test
In addition to those identified from MELCOR Assessment Report
  Fire test –LLNL Enclosure Fire – from Validation document of CFAST
  Aerosol resuspension test – STORM SR-11 Test
  Additional experiments from DOE-HDBK-3010-94
    Wind Tunnel Gasoline pool fire tests conducted at the RART facility
    Spills and Pressurized Release Tests conducted in RART
Verification
  Sample problems in MELCOR 1.8.5 guidance report
Version-to-version comparison: MELCOR 1.8.5, 1.8.6 and 2.1

## Slide 7: Multi-Room Fire Validation Study
Funded by LANL SB group
Assess MELCOR thermal-hydraulic response in multi-room fire
Assess smoke/contaminant aerosol transport
  Light smoke particle (hydrocarbon)
  Heavy contaminant particle (i.e., PuO2)
Use NIST NBS-GCR-502 FM21 Test to validate MELCOR
  Part of CFAST validation suite
  Thermal hydraulic validation
  CCF model:
  Aerosol transport of smoke/contaminants
Heat Release Rate from Propylene Combustion

## Slide 8: FM21Test – MELCOR Model
Control Volume setup to support:
Counter-current flow through door
Circulatory flow within room
[Tan 1992]
Control Volume setup to support stratified aerosol transport

## Slide 9: THERMAL-HYDRAULIC RESULTS (FM21 STUDY)
Counter Current Flow
Hot Gas Layer Temperature Comparison
Experimental and predicted trends (Case 0) agree
Door counter-current flow not measured in experiment
Predicted counter-current flow agrees with expected flow behavior
∆P between BR and Adjacent Corridor
Oxygen
composition
in Burn Room

## Slide 10: SMOKE & CONTAMINANT INPUTS (FM21 STUDY)
Cont.
Puff
*Assumed. Smoke is typically irregular shaped+ and ranges between 1 to 2 g/cc.
Production rate of 0.095 smoke mass per mass of fuel (g/g-fuel) [Butler 2004]
We did small sets of sensitivity studies on smoke only, UO2 and combination
Irregular shaped soot particles [Xu 2017]
Assumed UO2 release rate options

## Slide 11: SMOKE TRANSPORT RESULTS (FM21 STUDY)
General trend agreement (with exceptions) between experimental opacity and MELCOR smoke concentration (Case 4)
Notes: We assume a density of 0.8 g/cc for smoke in MELCOR calculation, and shape factor of 1.

## Slide 12: AEROSOL RESULTS (FM21 STUDY)
TR1
TR2

## Slide 13: SUMMARY AND CONCLUSIONS (FM21 STUDY)
Thermal hydraulic response
  MELCOR can model fire scenario, even through it does not contain a dynamic hot gas layer by using stratified control volumes
  Combustible burn can be modeled to allow better treatment of oxygen condition
  Counter-current flow model enables fire-room door counter-current flow
Smoke transport response
  MELCOR agrees well with FM21 smoke data
  Irregularly shaped particulate can be modeled by adjusting density and shape factor
Modeling insights associated with smoke, UO2 deposition and environmental release
  Higher density increases deposition
  Particulate size is a major contributor to gravitational settling
  MELCOR single aerosol density limitation can be overcome by use of particle size smear density adjustment method
  Instantaneous sourcing yields a lower environmental release

## Slide 14: FUTURE MELCOR NUCLEAR FACILITY SAFETY IDEAS
Sandia commits to expand MELCOR for active support to DOE facility safety
  Hope to engage more safety analysts at DOE to utilize MELCOR for LPF applications and update old MELCOR calculations in the current DSAs, if any
  Engage with DOE-AU32 to ensure that the latest version of MELCOR is in the DOE Central Registry
  Conduct MELCOR training on LPF applications to EFCOG members
    Successfully conducted 2 a week-long in-person MELCOR workshops at LANL
    Will notify community of similar MELCOR workshops once in-person activity is allowed
  Continue to support LANL SB group on MELCOR model review activity
  Like to propose to form a MELCOR user group (FMUG, Facility safety MELCOR User Group) for facility safeties in EFCOG
Other applications for MELCOR
  Support facility upgrade and new facility design

## Slide 15: What MELCOR stands for?
Although the name “MELCOR” is occasionally and incorrectly said to be an acronym for “Methods for Estimation of Leakages and Consequence of Releases,” it is actually a portmanteau derived from “MELting CORe.”
THANK YOU!!!
Notes: DOE-HDBK-1224-2018 is referred MELCOR as Methods for Estimation of Leakages and Consequences of Release.