## Risk Assessment Tool
|  | Shock Exposure | Shock Analysis |  |  |  | Arc Flash Analysis |  |  | Risk Matrix |  |  | Risk | Oversight Matrix | [5 empty] | Shock Analysis |  |  |  | Arc Flash Analysis
| Task | Exposed and Energized >50V | Shock Hazard <150Vac | Shock Hazard 151 - 750Vac | Shock Hazard 751 - 15kV | Shock Hazard >15kV | Arc Flash Hazard <1.2 cal/cm2 | Arc Flash Hazard 1.2 to 12 cal/cm2 | Arc Flash Hazard >12 cal/cm2 | Severity | Likelihood | Risk Score | Risk Level | Additional Worker | Crew Chief / Lead Worker | Foreman / Supervisor | Safety | Engineer / Planner | Line Manager | Shock Hazard <150Vac | Shock Hazard 151 to 750Vac | Shock Hazard 751 to 15kV | Shock Hazard >15kV | <1.2 Cal/cm2 | 1.2 - 12 Cal/cm2 | >12 Cal/cm2
1 | Transformer Visual Inspection (not crossin MAD) | No | [5 empty] | 7.6 |  | 2 | 1 | 2 | LOW | * | * | A, B | * | * | *
2 | Applying Grounds (15kV system) | Yes |  |  | 15000 |  |  | 4.8 |  | 3 | 4 | 12 | MEDIUM | A, C | A, C | A, B, C | A, * | A | *
3 | Manually racking breaker | Yes |  |  | 13800 |  |  |  | 23.1 | 4 | 4 | 16 | HIGH | A, C | A, C | A, D | A, C | A, C | * | 5 | 151 | 751 | 15001 | 0.1 | 1.2 | 13
[20 empty] | 10 | 160 | 1000 | 18000 | 0.2 | 1.3 | 14
[20 empty] | 20 | 175 | 1200 | 20000 | 0.3 | 1.4 | 15
[20 empty] | 24 | 200 | 1500 | 22500 | 0.4 | 1.5 | 16
[20 empty] | 25 | 208 | 2000 | 25000 | 0.5 | 1.6 | 17
[20 empty] | 30 | 220 | 2250 | 30000 | 0.6 | 1.7 | 18
[20 empty] | 35 | 240 | 2500 | 69000 | 0.7 | 1.8 | 19
A | Involved in pre-job and/or package walk down | [18 empty] | 40 | 277 | 2750 | 115000 | 0.8 | 1.9 | 20
B | Periodic/random job involvement or oversight | [18 empty] | 45 | 480 | 3000 | 125000 | 0.9 | 2 | 21
C | On the job for the Risk element of the task | [18 empty] | 48 | 600 | 4160 | 150000 | 1 | 2.1 | 22
D | Full task oversight | [18 empty] | 50 | 750 | 5000 | 230000 | 1.1 | 2.2 | 23
[20 empty] | 55 |  | 7620 | 500000 |  | 2.3 | 24
*May be required per site requirements | [19 empty] | 60 |  | 8000 | 1000000 |  | 2.4 | 25
**Additional worker should be a qualfied worker for the equipment and task | [19 empty] | 65 |  | 10000 |  |  | 2.5 | 26
[20 empty] | 70 |  | 11500 |  |  | 2.6 | 27
[20 empty] | 75 |  | 12470 |  |  | 2.7 | 28
[20 empty] | 80 |  | 13200 |  |  | 2.7 | 29
[20 empty] | 85 |  | 15000 |  |  | 2.9 | 30
[20 empty] | 90 |  |  |  |  | 3 | 31
[20 empty] | 95 |  |  |  |  | 3.1 | 32
[20 empty] | 100 |  |  |  |  | 3.2 | 33
[20 empty] | 105 |  |  |  |  | 3.3 | 34
[20 empty] | 110 |  |  |  |  | 3.4 | 35
[20 empty] | 115 |  |  |  |  | 3.5 | 36
[20 empty] | 120 |  |  |  |  | 3.6 | 37
[20 empty] | 125 |  |  |  |  | 3.7 | 38
[20 empty] | 130 |  |  |  |  | 3.8 | 39
[20 empty] | 135 |  |  |  |  | 3.9 | 40
[20 empty] | 140 |  |  |  |  | 4 | DANGEROUS!
[20 empty] | 145 |  |  |  |  | 4.1
[20 empty] | 150 |  |  |  |  | 4.2
4.3
4.4
4.5
4.6
4.7
4.8
4.9
5
5.1
5.2
5.3
5.4
5.5
5.6
5.7
5.8
5.9
6
6.1
6.2
6.3
6.4
6.5
6.6
6.7
6.8
6.9
7
7.1
7.2
7.3
7.4
7.5
7.6
7.7
7.8
7.9
8
8.1
8.2
8.3
8.4
8.5
8.6
8.7
8.8
8.9
9
9.1
9.2
9.3
9.4
9.5
9.6
9.7
9.8
9.9
10
10.1
10.2
10.3
10.4
10.5
10.6
10.7
10.8
10.9
11
11.1
11.2
11.3
11.4
11.5
11.6
11.7
11.8
11.9
12

## Oversight Matrix
Level of Risk | Additional Worker | Crew Chief / Lead Worker | Foreman / Supervisor | Safety | Engineer / Planner | Line Manager
LOW | * | * | A, B | * | * | *
MEDIUM | A, C | A, C | A, B, C | A, * | A | *
HIGH | A, C | A, C | A, D | A, C | A, C | *
A: Involved in pre-job and/or package walk down
B: Periodic/random job involvement or oversight
C: On the job for the Risk element of the task
D: Full task oversight
* May be required per site requirements
** Additional worker to be a qualified worker for the equipment, task, and/or potential rescue.

## Risk Assessment Matrix
Severity | Consequence |  |  | Probability – Increasing Likelihood
|  |  |  | 1 | 2 | 3 | 4 | 5
| People | Equipment | Environment | Event never heard of in the industry | Event heard of in the industry | Event has occurred in similar company | Event happens several times per year | Event occurs several times per year in a specific location
1 | No health effects or injury | No damage | No effect | 1 | 2 | 3 | 4 | 5
2 | Slight health effect of injury (first aid) | Minor damage | Minor effect | 2 | 4 | 6 | 8 | 10
3 | Minor health effect of injury (outpatient) | Localized damage | Contained effects | 3 | 6 | 9 | 12 | 15
4 | Major injury requiring surgery, hospitalization or extensive treatments | Major damage | Uncontained effects | 4 | 8 | 12 | 16 | 20
5 | Fatalities | Extensive damage | Extensive Geographic effects | 5 | 10 | 15 | 20 | 25
Low 1 - 6 |  |  | Medium 7 - 12 |  |  | High 13 - 25