## Doan DC
Arc Flash Energy - DC Bus - Max Energy Point - Linear Systems
Enter data in blue cells - Read answers in orange cells
This is a physics estimate only. It is not based on experimental data but has been verified
to be a conservative calculation of incident energy. Please note that this will show the
maximum incident energy possible based on the inputs. This method also uses the
conservative rounding of coefficients used by Doan [1] and NFPA 70E-2015 Section
D.5.1 [2]. Closed box approximations based on NFPA 70E-2015 Section D.5.1 or the calculated
closed box approximation from Wilkins, et. al. [3] as described by Ammerman, et. al. [4] are
available using the radio buttons.
Caution: These equations are based on maximum power point for a linear system and
will not represent non-linear systems accurately such as Photovoltaic systems or Voltage
Regulated systems such as battery chargers, UPS rectifiers or VFD buses under load.
Higher incident energy values may occur if clearing time increases due to the time current
curve (TCC) characteristics of any protective devices.
4
Vsys | 550 | V | [system open circuit voltage]
Ibf batt | 3000 | A | [bolted fault short circuit current listed for battery type]
N | 1 |  | [number of parallel battery strings]
Rcab | 0.002 | W | [resistance of cabling and connectors per string]
Ibf | 2967.6259 | A | [bolted fault short circuit current]
Iarc | 1483.8129 | A | [arcing current for maximum power point]
Tarc | 2 | s | [arc clearing time]
D | 45.5 | cm | [working distance]
| 17.9134 | in
CFWD | 2.2115 |  | [configuration factor at working distance]
CFAFB | 3.8031 |  | [configuration factor at arc flash boundary] |  | CFAFB | 2.2115 | 3.7227 | 3.8006 | 3.803 | 3.8031 | 3.8031 | 3.8031 | 3.8031 | 3.8031 | 3.8031 | 3.8031 | 3.8031 | 3.8031 | 3.8031 | 3.8031 | 3.8031 | 3.8031 | 3.8031 | 3.8031 | 3.8031 | 3.8031
IEm | 17.4357 | cal/cm2 |  |  | IEm | 17.4357 | 29.3498 | 29.9641 | 29.983 | 29.9835 | 29.9835 | 29.9835 | 29.9835 | 29.9835 | 29.9835 | 29.9835 | 29.9835 | 29.9835 | 29.9835 | 29.9835 | 29.9835 | 29.9835 | 29.9835 | 29.9835 | 29.9835 | 29.9835
AFB | 227.4376 | cm | 89.5424 | in | AFB | 173.4366 | 225.0212 | 227.364 | 227.4354 | 227.4375 | 227.4376 | 227.4376 | 227.4376 | 227.4376 | 227.4376 | 227.4376 | 227.4376 | 227.4376 | 227.4376 | 227.4376 | 227.4376 | 227.4376 | 227.4376 | 227.4376 | 227.4376 | 227.4376
References
[1] NFPA 70E, Standard for Electrical Safety in the Workplace,2015
[2] "Arc Flash Calculations for Exposures to DC Systems," Doan, D.R.,
IEEE Transactions on Industrial Applications, Vol. 46, No. 6.
[3] "Simple Improved Equations for Arc Flash Analysis," Wilkins, R.,
IEEE Electrical Safety Forum, posted August 30, 2004.
[4] "DC-Arc Models and Incident-Energy Calculations," Ammerman, R.F.; et al.;
IEEE Transactions on Industrial Applications, Vol. 46, No. 5.
Open Air
Closed Box - NFPA 70E 2015 D.5.1
Closed Box - Wilkins - Large Switchgear (MV) (1143mm x 762mm x 762mm)
Closed Box - Wilkins - Medium Switchgear (LV) (508mm x 508mm x 508mm)
Closed Box - Wilkins - Small Panel (LV) (305mm x 356mm x 191mm)

## SO DC
Arc Flash Energy - DC Bus - Stokes & Oppenlander - Linear Systems
Enter data in blue cells - Read answers in orange cells
This is an improved estimate. This will include an estimate of the effects of Gap on the
incident energy of the Stokes & Oppenlander equation as described by Ammerman, et. al. [4].
This method also uses the conservative rounding of coefficients used by Doan [1].
Closed box approximations based on NFPA 70E-2015 Section D.5.1 or the calculated
closed box approximation from Wilkins, et. al. [3] as described by Ammerman, et. al. [4] are
available using the radio buttons. |  |  |  |  | Stokes & Oppenlander Recursion
Caution: These equations are based on a manually entered estimate of gap and may |  |  |  |  | Varc | Iarc | Rarc
represent only linear systems accurately. Higher incident energy values may occur if clearing |  |  |  |  | 82.2139 | 1747.0588 | 0.047058
time increases due to the time current curve (TCC) characteristics of any protective devices. |  |  |  |  | 81.658 | 1651.0096 | 0.049459
[5 empty] | 81.6696 | 1652.9719 | 0.049408
| 1 |  |  |  | 81.6693 | 1652.9308 | 0.049409
[5 empty] | 81.6694 | 1652.9317 | 0.049409
[5 empty] | 81.6694 | 1652.9317 | 0.049409
[5 empty] | 81.6694 | 1652.9317 | 0.049409
[5 empty] | 81.6694 | 1652.9317 | 0.049409
[5 empty] | 81.6694 | 1652.9317 | 0.049409
Vsys | 550 | V | [system open circuit voltage] |  | 81.6694 | 1652.9317 | 0.049409
Varc | 81.6694 | V | [arcing voltage estimated from Stokes & Oppenlander] |  | 81.6694 | 1652.9317 | 0.049409
VF | 14.85% |  | [voltage factor - ratio of arcing to system voltage] |  | 81.6694 | 1652.9317 | 0.049409
Ibf batt | 3000 | A | [bolted fault short circuit current listed for battery type] |  | 81.6694 | 1652.9317 | 0.049409
N | 1 |  | [number of parallel battery strings] |  | 81.6694 | 1652.9317 | 0.049409
Rcab | 0.1 | W | [resistance of cabling and connectors per string] |  | 81.6694 | 1652.9317 | 0.049409
Ibf | 1941.1765 | A | [bolted fault short circuit current] |  | 81.6694 | 1652.9317 | 0.049409
Iarc | 1652.9317 | A | [arcing current estimated from Stokes & Oppenlander] |  | 81.6694 | 1652.9317 | 0.049409
It | 15.08 | A | [minimum arcing current for transition point] |  | 81.6694 | 1652.9317 | 0.049409
Vt | 46.4811 | V | [minimum arcing voltage for transition point] |  | 81.6694 | 1652.9317 | 0.049409
IF | 85.15% |  | [current factor - ratio of arcing to system current] |  | 81.6694 | 1652.9317 | 0.049409
Rsys | 0.28333 | W | [System resistance - bolted fault V/I] |  | 81.6694 | 1652.9317 | 0.049409
G | 25.4 | mm | [Arc Gap in mm] |  | 81.6694 | 1652.9317 | 0.049409
| 1 | in |  |  | 81.6694 | 1652.9317 | 0.049409
Tarc | 2 | s | [arc clearing time]
D | 45.5 | cm | [working distance]
| 17.9134 | in
Narc | 0.50576 |  | [Arc Efficiency - Percent of Maximum Available Energy]
CFWD | 1 |  | [configuration factor at working distance] |  | CFAFB | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
CFAFB | 1 |  | [configuration factor at arc flash boundary] |  | IEm | 2.6083 | 2.6083 | 2.6083 | 2.6083 | 2.6083 | 2.6083 | 2.6083 | 2.6083 | 2.6083 | 2.6083 | 2.6083 | 2.6083 | 2.6083 | 2.6083 | 2.6083 | 2.6083 | 2.6083 | 2.6083 | 2.6083 | 2.6083 | 2.6083
IEm | 2.6083 | cal/cm2 |  |  | AFB | 67.0805 | 67.0805 | 67.0805 | 67.0805 | 67.0805 | 67.0805 | 67.0805 | 67.0805 | 67.0805 | 67.0805 | 67.0805 | 67.0805 | 67.0805 | 67.0805 | 67.0805 | 67.0805 | 67.0805 | 67.0805 | 67.0805 | 67.0805 | 67.0805
AFB | 67.0805 | cm | 26.4097 | in
References
[1] NFPA 70E, Standard for Electrical Safety in the Workplace,2015
[2] "Arc Flash Calculations for Exposures to DC Systems," Doan, D.R.,
IEEE Transactions on Industrial Applications, Vol. 46, No. 6.
[3] "Simple Improved Equations for Arc Flash Analysis," Wilkins, R.,
IEEE Electrical Safety Forum, posted August 30, 2004.
[4] "DC-Arc Models and Incident-Energy Calculations," Ammerman, R.F.; et al.;
IEEE Transactions on Industrial Applications, Vol. 46, No. 5.
Open Air
Closed Box - NFPA 70E 2015 D.5.1
Closed Box - Wilkins - Large Switchgear (MV) (1143mm x 762mm x 762mm)
Closed Box - Wilkins - Medium Switchgear (LV) (508mm x 508mm x 508mm)
Closed Box - Wilkins - Small Panel (LV) (305mm x 356mm x 191mm)

## Cap 1
Arc Flash Energy - Capacitor - Stored Energy
Enter data in blue cells - Read answers in orange cells
This is a physics estimate only. It is not based on experimental data but has been verified
to be a conservative calculation of incident energy. Please note that this will show the
maximum incident energy possible based on the inputs. This method also uses the
conservative rounding of coefficients used by Doan [1] and NFPA 70E-2015 Section
D.5.1 [2]. Closed box approximations based on NFPA 70E-2015 Section D.5.1 or the calculated
closed box approximation from Wilkins, et. al. [3] as described by Ammerman, et. al. [4] are
available using the radio buttons.
Also included for capacitor calculation is an estimated damage radius for ear or lung damage
at the 1% susceptability threshold. Calculation is based on the Army Research Lab (ARL)
estimate from blast modeling of equivalent energy using Air_Blast_Lethality code as described
in reference [5]. 1% ear damage corresponds to 3 psi overpressure or 180dB SPL. 1% lung
damage corresponds to 10 psi overpressure.
2
Vpeak | 20000 | V | [peak open circuit voltage]
C | 1000 | uF | [capacitance in microfarads]
E | 200 | kJ | [stored energy in kilojoules]
D | 92 | cm | [working distance]
| 36.2205 | in
CFWD | 3 |  | [configuration factor at working distance]
CFAFB | 3 |  | [configuration factor at arc flash boundary] |  | CFAFB | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
IEm | 1.4178 | cal/cm2 |  |  | IEm | 1.4178 | 1.4178 | 1.4178 | 1.4178 | 1.4178 | 1.4178 | 1.4178 | 1.4178 | 1.4178 | 1.4178 | 1.4178 | 1.4178 | 1.4178 | 1.4178 | 1.4178 | 1.4178 | 1.4178 | 1.4178 | 1.4178 | 1.4178 | 1.4178
AFB | 100 | cm | 39.3701 | in | AFB | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Lung 1% | 24.5041 | cm | 9.6473 | in
Ear 1% | 278.1136 | cm | 109.4935 | in
References
[1] NFPA 70E, Standard for Electrical Safety in the Workplace,2015
[2] "Arc Flash Calculations for Exposures to DC Systems," Doan, D.R.,
IEEE Transactions on Industrial Applications, Vol. 46, No. 6.
[3] "Simple Improved Equations for Arc Flash Analysis," Wilkins, R.,
IEEE Electrical Safety Forum, posted August 30, 2004.
[4] "DC-Arc Models and Incident-Energy Calculations," Ammerman, R.F.; et al.;
IEEE Transactions on Industrial Applications, Vol. 46, No. 5.
[5] "Safe Distances From a High-Energy Capacitor Bank for Ear and Lung Protection"
Hummer, Charles R.; et al.; Army Research Laboratory ARL-TN-608, June 2014.
Open Air
Closed Box - NFPA 70E 2015 D.5.1
Closed Box - Wilkins - Large Switchgear (MV) (1143mm x 762mm x 762mm)
Closed Box - Wilkins - Medium Switchgear (LV) (508mm x 508mm x 508mm)
Closed Box - Wilkins - Small Panel (LV) (305mm x 356mm x 191mm)

## Cap 2
Arc Flash Protection Boundary is the onset of a second degree burn at a flux of (1.2 cal/cm^2 --- 5 J/cm^2)
This approach follows the method from the DOE Electrical Safety Workshop July 16-20 2007. It uses a 3x factor (to accommodate the focusing of energy due to a deep enclosure) of the 3d symmetrically propagated energy solved for a 2nd degree burn energy density of 5J/cm^2: Dc = sqrt(0.05 x E)
| Dc [in] | E [J] | E [J] | Dc [in] | Dc [ft]
| 1 | 20 | 10 | 0.70711 | 0.058926
| 6 | 720 | 100 | 2.2361 | 0.18634
| 12 | 2880 | 1000 | 7.0711 | 0.58926
| 18 | 6480 | 10000 | 22.3607 | 1.8634
| 36 | 25920 | 100000 | 70.7107 | 5.8926
| 72 | 103680 | 1000000 | 223.6068 | 18.6339
| 96 | 184320 | 10000000 | 707.1068 | 58.9256
| 115.4179 | 266425.9076
| 36.2205 | 200000 | No AR
97.6729
No AR
|  |  | 38.4726 | D53
|  |  | 38.4726 | no IF
|  |  | 0.018798 | no SQRT
|  |  | 0.047746 | metric
If the Flash Protection Boundary (Dc) calculated by this method results in a distance that is greater than the distance at which the worker must approach the energy storage element, scale the distance using the Step 2 table below to find the energy density exposure for the worker at the working distance. (Step 2) Enter the distance from the worker's body to the hazard into the light green cell (Working Distance Dw [in]). Appendix E data is duplicated in the formula to determine the Risk Category as a function of Energy Density (ATPV). The table also shows the clothing label information that is appropriate for the required ATPV.
|  | Arc-in-a-Box |  |  |  | no-Arc-in-a-Box
| E [J] | Dc [in] | Dc [ft] |  |  | Dc [in] | Dc [ft]
Step 1 | 200000 | 100 | 8.3 |  |  | 57.735 | 4.8
| Working Distance Dw [in] | ATPV [cal/cm^2] | Risk Category | Clothing Label [cal/cm^2] |  | ATPV [cal/cm^2] | Risk Category | Clothing Label [cal/cm^2]
Step 2 | 36.2205 | 9.1 | 3 | 25 |  | 3 | 1 | 4
|  | Working Distance Dw min [in] | ATPV [cal/cm^2] | Risk Category | Clothing Label [cal/cm^2] | Working Distance Dw min [in] | ATPV [cal/cm^2] | Risk Category | Clothing Label [cal/cm^2]
|  | 100 | 1.2 | 0 | 1.2 | 57.735 | 1.2 | 0 | 1.2
|  | 54.7723 | 4 | 1 | 4 | 31.6228 | 4 | 1 | 4
|  | 38.7298 | 8 | 2 | 8 | 22.3607 | 8 | 2 | 8
|  | 21.9089 | 25 | 3 | 25 | 12.6491 | 25 | 3 | 25
|  | 17.3205 | 40 | 4 | 40 | 10 | 40 | 4 | 40
|  | 17.2205 | > 40 | No Hot Work | No Hot Work | 9.9 | > 40 | No Hot Work | No Hot Work

## Ind 1
Arc Flash Energy - Inductor - Stored Energy
Enter data in blue cells - Read answers in orange cells
This is a physics estimate only. It is not based on experimental data but has been verified
to be a conservative calculation of incident energy. Please note that this will show the
maximum incident energy possible based on the inputs. This method also uses the
conservative rounding of coefficients used by Doan [1] and NFPA 70E-2015 Section
D.5.1 [2]. Closed box approximations based on NFPA 70E-2015 Section D.5.1 or the calculated
closed box approximation from Wilkins, et. al. [3] as described by Ammerman, et. al. [4] are
available using the radio buttons.
Also included for inductor calculation is an estimated damage radius for ear or lung damage
at the 1% susceptability threshold. Calculation is based on the Army Research Lab (ARL)
estimate from blast modeling of equivalent energy using Air_Blast_Lethality code as described
in reference [5]. 1% ear damage corresponds to 3 psi overpressure or 180dB SPL. 1% lung
damage corresponds to 10 psi overpressure.
1
I | 200 | A | [peak system initial circuit current]
L | 10000 | mH | [inductance in millihenries]
E | 200 | kJ | [stored energy in kilojoules]
D | 45.5 | cm | [working distance]
| 17.9134 | in
CFWD | 1 |  | [configuration factor at working distance]
CFAFB | 1 |  | [configuration factor at arc flash boundary] |  | CFAFB | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
IEm | 1.9321 | cal/cm2 |  |  | IEm | 1.9321 | 1.9321 | 1.9321 | 1.9321 | 1.9321 | 1.9321 | 1.9321 | 1.9321 | 1.9321 | 1.9321 | 1.9321 | 1.9321 | 1.9321 | 1.9321 | 1.9321 | 1.9321 | 1.9321 | 1.9321 | 1.9321 | 1.9321 | 1.9321
AFB | 57.735 | cm | 22.7303 | in | AFB | 57.735 | 57.735 | 57.735 | 57.735 | 57.735 | 57.735 | 57.735 | 57.735 | 57.735 | 57.735 | 57.735 | 57.735 | 57.735 | 57.735 | 57.735 | 57.735 | 57.735 | 57.735 | 57.735 | 57.735 | 57.735
Lung 1% | 24.5041 | cm | 9.6473 | in
Ear 1% | 278.1136 | cm | 109.4935 | in
References
[1] NFPA 70E, Standard for Electrical Safety in the Workplace,2015
[2] "Arc Flash Calculations for Exposures to DC Systems," Doan, D.R.,
IEEE Transactions on Industrial Applications, Vol. 46, No. 6.
[3] "Simple Improved Equations for Arc Flash Analysis," Wilkins, R.,
IEEE Electrical Safety Forum, posted August 30, 2004.
[4] "DC-Arc Models and Incident-Energy Calculations," Ammerman, R.F.; et al.;
IEEE Transactions on Industrial Applications, Vol. 46, No. 5.
[5] "Safe Distances From a High-Energy Capacitor Bank for Ear and Lung Protection"
Hummer, Charles R.; et al.; Army Research Laboratory ARL-TN-608, June 2014.
[7] Wiley Engineer's Desk Reference, Second Edition, Heisler, Sanford I., P.E., John
Wiley & Sons, Inc., c. 1998.
Open Air
Closed Box - NFPA 70E 2015 D.5.1
Closed Box - Wilkins - Large Switchgear (MV) (1143mm x 762mm x 762mm)
Closed Box - Wilkins - Medium Switchgear (LV) (508mm x 508mm x 508mm)
Closed Box - Wilkins - Small Panel (LV) (305mm x 356mm x 191mm)

## Ind 2
Arc Flash Energy - Inductor - Solenoid Superconductors
Enter data in blue cells - Read answers in orange cells
This is a physics estimate only. It is not based on experimental data but has been verified
to be a conservative calculation of incident energy. Please note that this will show the
maximum incident energy possible based on the inputs. This method also uses the
conservative rounding of coefficients used by Doan [1] and NFPA 70E-2015 Section
D.5.1 [2]. Closed box approximations based on NFPA 70E-2015 Section D.5.1 or the calculated
closed box approximation from Wilkins, et. al. [3] as described by Ammerman, et. al. [4] are
available using the radio buttons.
Also included for inductor calculation is an estimated damage radius for ear or lung damage
at the 1% susceptability threshold. Calculation is based on the Army Research Lab (ARL)
estimate from blast modeling of equivalent energy using Air_Blast_Lethality code as described
in reference [5]. 1% ear damage corresponds to 3 psi overpressure or 180dB SPL. 1% lung
damage corresponds to 10 psi overpressure.
1
B | 10 | T | [maximum magnetic field in tesla]
l | 0.5 | m | [length of coil in meters]
d | 0.2 | m | [diameter of coil in meters]
E | 624.819 | kJ | [stored energy in kilojoules]
D | 45.5 | cm | [working distance]
| 17.9134 | in
CFWD | 1 |  | [configuration factor at working distance]
CFAFB | 1 |  | [configuration factor at arc flash boundary] |  | CFAFB | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
IEm | 6.0362 | cal/cm2 |  |  | IEm | 6.0362 | 6.0362 | 6.0362 | 6.0362 | 6.0362 | 6.0362 | 6.0362 | 6.0362 | 6.0362 | 6.0362 | 6.0362 | 6.0362 | 6.0362 | 6.0362 | 6.0362 | 6.0362 | 6.0362 | 6.0362 | 6.0362 | 6.0362 | 6.0362
AFB | 102.0473 | cm | 40.1761 | in | AFB | 102.0473 | 102.0473 | 102.0473 | 102.0473 | 102.0473 | 102.0473 | 102.0473 | 102.0473 | 102.0473 | 102.0473 | 102.0473 | 102.0473 | 102.0473 | 102.0473 | 102.0473 | 102.0473 | 102.0473 | 102.0473 | 102.0473 | 102.0473 | 102.0473
Lung 1% | 106.622 | cm | 41.9772 | in
Ear 1% | 407.3471 | cm | 160.3729 | in
References
[1] NFPA 70E, Standard for Electrical Safety in the Workplace,2015
[2] "Arc Flash Calculations for Exposures to DC Systems," Doan, D.R.,
IEEE Transactions on Industrial Applications, Vol. 46, No. 6.
[3] "Simple Improved Equations for Arc Flash Analysis," Wilkins, R.,
IEEE Electrical Safety Forum, posted August 30, 2004.
[4] "DC-Arc Models and Incident-Energy Calculations," Ammerman, R.F.; et al.;
IEEE Transactions on Industrial Applications, Vol. 46, No. 5.
[5] "Safe Distances From a High-Energy Capacitor Bank for Ear and Lung Protection"
Hummer, Charles R.; et al.; Army Research Laboratory ARL-TN-608, June 2014.
[7] Wiley Engineer's Desk Reference, Second Edition, Heisler, Sanford I., P.E., John
Wiley & Sons, Inc., c. 1998.
[8] Electromagnetism Maxwell Equations, Wave Propogation and Emmision,
Bécherrawy, Tamer, John Wiley & Sons, Inc., c. 2012.
Open Air
Closed Box - NFPA 70E 2015 D.5.1
Closed Box - Wilkins - Large Switchgear (MV) (1143mm x 762mm x 762mm)
Closed Box - Wilkins - Medium Switchgear (LV) (508mm x 508mm x 508mm)
Closed Box - Wilkins - Small Panel (LV) (305mm x 356mm x 191mm)

## MSO PV
Arc Flash Energy - Modified Stokes & Oppenlander - PV Systems
Enter data in blue cells - Read answers in orange cells
This is an improved estimate. This will include an estimate of the effects of Gap on the
incident energy of the Stokes & Oppenlander equation as described by Ammerman, et. al. [4].
The Stokes & Oppenlander numbers are modified for expanded arc in a non-linear PV system
as described in Sekulic, Maroquin and McNutt [5].
This method also uses the conservative rounding of coefficients used by Doan [1].
Closed box approximations based on NFPA 70E-2015 Section D.5.1 or the calculated
closed box approximation from Wilkins, et. al. [3] as described by Ammerman, et. al. [4] are
available using the radio buttons.
Caution: These equations are based on a manually entered estimate of gap and an
an upper bound of arcing current based on short circuit PV current. Effects based on OCPD's
may have little effect on PV devices due to the nature of short circuits with this technology.
4
Vmod | 31 |  | [module max power voltage]
N | 25 |  | [modules in series in system]
Vsys | 775 | V | [system operating voltage]
Rarc | 0.79566 | W | [resistance of arc from Sekulic, Marroquin & McNutt]
Varc | 102.5251 | V | [arcing voltage from Sekulic, Marroquin & McNutt]
VF | 13.23% |  | [voltage factor - ratio of arcing to system voltage]
Isc mod 0 | 9.58 | A | [short circuit current per module]
KT-ISC | 0.04% | /°C | [temperature coefficient]
Tmax | 85 | °C | [max temperature]
TF | 102.4% |  | [temperature factor]
ISTC | 1000 | W/m2 | [rated standard irradiance from specifications]
h | 1000 | m | [elevation of array in meters]
| 3280.84 | ft | [elevation of array in feet]
IG | 1094.6003 |  | [calculated maximum global irradiance with AM=1]
EF | 109.5% |  | [irradiance factor]
Isc mod | 10.7379 | A | [short circuit current per module adjusted]
M | 12 |  | [number of parallel module strings]
Isc sys | 128.8553 | A | [system short circuit current]
Iarc | 128.8553 | A | [arcing current estimated from Stokes & Oppenlander]
It | 15.08 | A | [minimum arcing current for transition point]
Vt | 46.4811 | V | [minimum arcing voltage for transition point]
IF | 100% |  | [current factor - ratio of arcing to system current]
G | 25.4 | mm | [Arc Gap in mm]
| 1 | in
Tarc | 2 | s | [arc clearing time]
D | 61 | cm | [working distance]
| 24.0157 | in
CFWD | 2.7418 |  | [configuration factor at working distance]
CFAFB | 1 |  | [configuration factor at arc flash boundary] |  | CFAFB | 2.7418 | 1.6862 | 1.2428 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
IEm | 0.38937 | cal/cm2 |  |  | IEm | 0.38937 | 0.23946 | 0.17649 | 0.14201 | 0.14201 | 0.14201 | 0.14201 | 0.14201 | 0.14201 | 0.14201 | 0.14201 | 0.14201 | 0.14201 | 0.14201 | 0.14201 | 0.14201 | 0.14201 | 0.14201 | 0.14201 | 0.14201 | 0.14201
AFB | 20.9848 | cm | 8.2617 | in | AFB | 34.7473 | 27.2495 | 23.3939 | 20.9848 | 20.9848 | 20.9848 | 20.9848 | 20.9848 | 20.9848 | 20.9848 | 20.9848 | 20.9848 | 20.9848 | 20.9848 | 20.9848 | 20.9848 | 20.9848 | 20.9848 | 20.9848 | 20.9848 | 20.9848
References
[1] NFPA 70E, Standard for Electrical Safety in the Workplace,2015
[2] "Arc Flash Calculations for Exposures to DC Systems," Doan, D.R.,
IEEE Transactions on Industrial Applications, Vol. 46, No. 6.
[3] "Simple Improved Equations for Arc Flash Analysis," Wilkins, R.,
IEEE Electrical Safety Forum, posted August 30, 2004.
[4] "DC-Arc Models and Incident-Energy Calculations," Ammerman, R.F.; et al.;
IEEE Transactions on Industrial Applications, Vol. 46, No. 5.
[5] "Methods for Evaluating DC Arc Incident Energy in PV Systems," Sekulic, William;
et al.; 2021 IEEE IAS Electrical Safety Workshop.
[6] Applied Solar Energy. A. B. Meinel and Meinel, M. P., Addison Wesley
Publishing Co., 1976.
[7] "The measurement of solar spectral irradiance at different terrestrial
elevations”, E. G. Laue, Solar Energy, vol. 13, pp. 43 - 50, IN1-IN4, 51-57, 1970.
Open Air
Closed Box - NFPA 70E 2015 D.5.1
Closed Box - Wilkins - Large Switchgear (MV) (1143mm x 762mm x 762mm)
Closed Box - Wilkins - Medium Switchgear (LV) (508mm x 508mm x 508mm)
Closed Box - Wilkins - Small Panel (LV) (305mm x 356mm x 191mm)

## Ref
Equations used in calculations for reference:
References
[1] NFPA 70E, Standard for Electrical Safety in the Workplace,2021
| D.5.1 | Iarc = 0.5 x Ibf
IEm = 0.01 x Vsys x Iarc x Tarc / D2
Iarc = arcing current (A)
Ibf = system bolted fault current (A)
IEm = estimated dc arc flash incident energy (cal/cm2)
Vsys = system voltage (V)
Tarc = arcing time (s)
D = working distance (cm)
[2] "Arc Flash Calculations for Exposures to DC Systems," Doan, D.R.,
IEEE Transactions on Industrial Applications, Vol. 46, No. 6, November/December 2010.
| (7) | IEmax power = 0.005 x (Vsys2 / Rsys) x Tarc / D2
IEmax power = estimated dc arc flash incident energy (cal/cm2)
Rsys = system resistance (W)
Vsys = system voltage (V)
Tarc = arcing time (s)
D = working distance (cm)
For arc in a box, multiply IEm by 3
[3] "Simple Improved Equations for Arc Flash Analysis," Wilkins, R.,
IEEE Electrical Safety Forum, posted August 30, 2004.
E1 = k * Earc / (a2 + d2)
E1 = incident energy adjusted for enclosure effects
Earc = open air incident energy
d = working distance (mm)
a & k values per the following table:
|  | Enclosure | Width (mm) | Height (mm) | Depth (mm) | a (mm) | k
|  | Panelboard | 305 | 356 | 191 | 100 | 0.127
|  | LV Switchgear | 508 | 508 | 508 | 400 | 0.312
|  | HV Switchgear | 1143 | 762 | 762 | 950 | 0.416
[4] "DC-Arc Models and Incident-Energy Calculations," Ammerman, R.F.; et al.;
IEEE Transactions on Industrial Applications, Vol. 46, No. 5, September/October 2010.
Stokes & Oppenlander
| (8) | Rarc = (20 + 0.534 * zg) / Iarc 0.88
It = 10 + 0.2 * zg
Rarc = arc resistance (W)
Iarc = arcing current (A)
zg = length of gap (mm)
It = transition current (A) = minimum current where equation holds
[5] "DC-Arc Flash Calculations for Solar Farms," Enrique, E.H.; et al.;
2013 IEEE Conference on Technologies for Sustainability.
| [13] | IEm = 0.02 x Varc x Iarc x Tarc / D2
| [14] | IEm comp = IEm * (1-KT Pmax) * (25°C - Tmin)
IEm = estimated dc arc flash incident energy
IEm comp = estimated temperature compensated dc arc flash incident energy
Varc = arcing voltage (V)
Iarc = arcing current (A)
Tarc = arcing time (s)
D = working distance (cm)
Tmin = minimum temperature (°C)
KT Pmax = temperature coefficient at max power point (°C-1)
[6] "Safe Distances From a High-Energy Capacitor Bank for Ear and Lung Protection"
Hummer, Charles R.; et al.; Army Research Laboratory ARL-TN-608, June 2014.
E= 0.5 * C * V2 / 1000
IE = 0.02 x Varc x Iarc x Tarc / D2
IE = 0.02 x E * 1000 / D2
| (1) | Rear = 49.29 * E1/3 - 5.09
| (2) | Rlung = 31.32 * E1/3 - 155.45
E = Capacitor Stored Energy (kJ)
C= Capacitance (C)
V = Stored Voltage (V)
Rear = Safe Distance from 1% chance of Ear Rupture
Rlung = Safe Distance from 1% chance of Lung Damage
[7] Wiley Engineer's Desk Reference, Second Edition, Heisler, Sanford I., P.E., John
Wiley & Sons, Inc., c. 1998.
| (6.25) | E = 0.5 * L * I2 / 1000
E = Inductor Stored Energy (kJ)
L= Inductance (H)
I = Initial Current (A)
[8] Electromagnetism Maxwell Equations, Wave Propogation and Emmision,
Bécherrawy, Tamer, John Wiley & Sons, Inc., c. 2012.
| (6.54) | B = m0 * n * I = m0 * N * I / l
B = Magnetic Field Strength (T)
l = Solenoid Length (m)
N = Number of turns
n = Number of turns per length (m-1) = N / l
I = Initial Current (A)
m0 = Magnetic Constant = 4p * 10-7 H/m
| (8.32) | L = m0 * N2 * p * r2 / l = m0 * N2 * p * d2 / 4 l
r = Solenoid Radius (m)
d = Solenoid Diameter (m) = r * 2
L / B2 = p * d2 * l / 4m0 / I2
E = 0.5 * L * I2 / 1000 = B2 * p * d2 * l / 8000m0
E = Inductor Stored Energy (kJ)
[9] Applied Solar Energy. A. B. Meinel and Meinel, M. P., Addison Wesley
Publishing Co., 1976.
ID = I0 * 0.7 AM ^ 0.678
AM = Air Mass : AM=1 for overhead maximum value
I0 = Total Solar Irradiance : Max I0 = 1397.6 W/m2 at perihelion
ID = Direct Irradiance
IG = 1.1 * ID
IG = Global Irradiance (takes scattering into account)
IG max = 1.1 * I0 * 0.7 = 1076.2 W/m2 when AM = 1
[10] "The measurement of solar spectral irradiance at different terrestrial
elevations”, E. G. Laue, Solar Energy, vol. 13, pp. 43 - 50, IN1-IN4, 51-57, 1970.
ID = I0 * [(1−ah) * 0.7AM^0.678+ah]
h = height in km
a = 0.14
IG max = 1.1 * I0 * [(1-ah) * 0.7 + ah]
[11] "Methods for Evaluating DC Arc Incident Energy in PV Systems," Sekulic, William;
et al.; 2021 IEEE IAS Electrical Safety Workshop.
Rarc = Rarc 0 [1 + aeb(t-Ti) h(t-Ti)]
Varc = Varc 0 [1 + aeb(t-Ti) h(t-Ti)]
Rarc = arc resistance (W)
Varc = arcing voltage (V)
Rarc 0 = arc resistance estimated from Stokes and Oppenlander [4] (W)
Varc 0 = arcing voltage estimated from Stokes and Oppenlander [4] (V)
a = Proportional arc elongation coefficient == 0.25 *
b = Exponential arc elongation coefficient == 0.525 *
Ti = Inception or arc ignition time (s) == 25 ms
h(t) = Heaviside Step Function
* revised constants a and b provided by personal correspondance from author
A. Marraquin on 12/14/2021to correct an error in the original paper.